## Quantity Takeoff
AutoZone Store #11074 — Tavares, FL
Electrical Quantity Takeoff — PRE-BID / INTERNAL (Counted, with Confidence)
GC: Summit General Contractors ¦ Job No.: JS.07292026 ¦ Prepared: 07/29/2026
Plan Date(s): Civil 02/23/26 ¦ Architectural/Structural/Mechanical/Plumbing/Electrical 04/15/26 (Rev 7N2-R)
Building area: 7,147 SF net interior ¦ 7,381 SF gross/perimeter footprint (Source: Code Analysis, sheet A0)
1. SERVICE & DISTRIBUTION
ITEM | DESCRIPTION | UNIT | QTY | CONF. | SOURCE / BASIS / NOTES
1 | Fused Disconnect Switch, 200A/3P, NEMA 3R (Discon A & Discon B) — OWNER FURNISHED, APT INSTALLED | EA | 2 | FIRM | E-4 Schematic One-Line / Load Totals
2 | Panelboard "Panel A", 225A bus, 208Y/120V 3P4W, MLO — OWNER FURNISHED, APT INSTALLED | EA | 1 | FIRM | E-4 Panel Schedule
3 | Panelboard "Panel B", 225A bus, 208Y/120V 3P4W, MLO — OWNER FURNISHED, APT INSTALLED | EA | 1 | FIRM | E-4 Panel Schedule
4 | Meter Base, NEMA 3R — APT (ECFECI) | EA | 1 | FIRM | E-4 Schematic One-Line
5 | Wireway, NEMA 3R (12x12x required length) — APT (ECFECI) | EA | 1 | FIRM | E-4 Schematic One-Line
6 | Service conductors & conduit: parallel (2) sets 4#3/0 & #6G in 2"C, meter to service equipment — APT (ECFECI) | LF | VERIFY | VERIFY | E-4 spec confirmed; run length not dimensioned — pull from Civil C4.1 utility routing
7 | Grounding/bonding system complete (ground rod, electrode conductor, building steel & water pipe bonds, equipment bonding) — APT (ECFECI) | LOT | 1 | FIRM | E-4 Detail 3 — Grounding/Bonding Diagram
8 | RTU-1 branch circuit: 60A/3P breaker, 3#6 & #10G in 3/4"C (conduit & wire only; unit & disconnect by mechanical) — APT (ECFECI) | EA | 1 | FIRM | E-4 Panel B ckt 1,3,5 / E-1
9 | RTU-2 branch circuit: 60A/3P breaker, 3#6 & #10G in 3/4"C — APT (ECFECI) | EA | 1 | FIRM | E-4 Panel B ckt 2,4,6 / E-1
2. INTERIOR LIGHTING (all fixtures OWNER FURNISHED — AutoZone; APT receives, inventories, installs)
ITEM | DESCRIPTION | UNIT | QTY | CONF. | SOURCE / BASIS / NOTES
10 | Type A — 8' LED Strip Fixture, 34W input, sales/work lighting | EA | 64 | APPROX | E-3 Lighting Plan, visual count of chained runs — range 58–70. Dense overlapping tags; recommend field verify or re-count from CAD if bid is close
11 | Type B — 8' LED Strip Fixture, 17W input | EA | 48 | APPROX | E-3 Lighting Plan, visual count — range 44–52
12 | Type C — 4' LED Strip Wall Light, 8.5W (office rooms) | EA | 2 | FIRM | E-3 Lighting Plan — office area, easily isolated count
13 | Type M — 4' LED Strip, 17W (bar-type unit, caps sales-floor column runs) | EA | 8 | APPROX | E-3 Lighting Plan — range 6–10
14 | Type N — 4' LED Strip, 8.5W (single-tube) | EA | 0 | VERIFY | Not clearly identified in visual count — confirm against Light Fixture Schedule (E-3, detail 4) whether used on this store
15 | Type G — 8" Gotham LED Soffit Downlight, 49W (entry soffit) | EA | 8 | FIRM | E-3 Lighting Plan visual count, cross-checked against E-4 Panel A ckt12 "Exterior Soffit Lighting" = 392VA ÷ 49W = 8 fixtures — confirmed
16 | Type E — Emergency Light w/ Battery Backup | EA | 12 | APPROX | E-3 Lighting Plan — range 10–15
17 | Type F — Exit Sign w/ Battery Backup, remote emergency head | EA | 4 | APPROX | E-3 Lighting Plan — range 3–5
18 | Type J — Exterior Emergency Light, two heads (entry door) | EA | 3 | APPROX | E-3 Lighting Plan — range 2–3
19 | Type K — Exit Sign w/ Battery Backup, interior mount to bar joist/unistrut | EA | 1 | VERIFY | Only one instance spotted in visual pass — confirm count against E-3 detail 4 schedule
20 | Ceiling Fan, Hunter #28692 w/ wall-mount speed controller #27180 — AutoZone furnished, APT installed & wired to sales floor light circuit | EA | 3 | FIRM | E-1 General Notes item 1 & E-3 Lighting Plan — labeled CF1, CF2, CF3
3. EXTERIOR / SITE LIGHTING (OWNER FURNISHED — AutoZone)
ITEM | DESCRIPTION | UNIT | QTY | CONF. | SOURCE / BASIS / NOTES
21 | D-Series Wall Pack, DSXW1 LED, 40W (Type D) — storefront-height exterior wall pack | EA | VERIFY | VERIFY | Not located on E-3 plan view (may be on exterior elevation A2, not in this excerpt). Panel A ckt13 "Exterior Building Lighting" = 214VA total (Types D+L combined) — confirm split/qty against A2
22 | D-Series Wall Pack, DSXW1 LED, 20W (Type L) — storefront-height exterior wall pack | EA | VERIFY | VERIFY | See Type D note above — combined 214VA circuit, quantity/type split not itemized in electrical set reviewed
23 | Site Light Pole, D-Series DSX1 LED, 209W, pole-mounted parking lot fixture | EA | VERIFY | VERIFY | E-4 Panel A shows 3 "Site Lighting" circuits @ 209VA each. E-2 note: "parking lot site lights typically have two fixtures per pole, wired two poles per circuit." Exact pole count/locations are on Civil Photometric Plan PH0.1 — NOT included in the electrical sheet set provided for this takeoff
4. LIGHTING CONTROLS (OWNER FURNISHED — AutoZone; APT installs & wires)
ITEM | DESCRIPTION | UNIT | QTY | CONF. | SOURCE / BASIS / NOTES
24 | Lighting Control Panel (LCP) w/ accessories, contactors, photocell | EA | 1 | FIRM | E-5 Lighting Control Panel and Details
25 | Occupancy Sensor, CMR-9 (restroom ceiling — connects to fan & light) | EA | 2 | FIRM | E-3 Light Fixture Schedule + Lighting Plan — one per restroom (2 restrooms per A1 floor plan)
26 | Motion Sensor for ALC Panel (circled "M" symbol) | EA | 1 | VERIFY | Listed in E-3 Light Fixture Schedule but not conclusively located in visual plan pass — confirm placement in field/plan detail
27 | Motion Sensor, 10-Minute, LSXR-50-HL (aisleway lens) | EA | 0 | VERIFY | E-3 schedule note: "Motion sensor M2 will be used in HUB and MEGA HUB stores only" — this is a standard store, likely N/A. Confirm store type before excluding
5. BRANCH POWER
ITEM | DESCRIPTION | UNIT | QTY | CONF. | SOURCE / BASIS / NOTES
28 | Interior Power Pole, freestanding w/ pre-wired duplex outlet(s) — Office (#1), Check-Out (#2), Parts Pod (#3), Tester (#4), Office (#5), Commercial Counter (#6) — APT (ECFECI) furnished & installed per Summit GC SOV | EA | 6 | FIRM | E-2, details 2–5, 9, 11 — Power Pole Legend & Notes
29 | Dedicated equipment & receptacle branch circuits, 20A/1P (water heater, CCTV monitor, POD sales terminals x2, alarm system, alarm receptacle, tel co, office training/III/UPS, EAS post & alarm, commercial receptacles x3, maint/OX-Blue receptacle, battery chargers x5, ALC panel, break room fridge, mini-tune, test accessories, drinking fountain, landscape control, general receptacle, drink machine) — APT (ECFECI) | CKT | 29 | FIRM | E-4 Panel A & Panel B schedules — direct circuit count
30 | Duplex / GFCI / weatherproof-GFCI / quadplex receptacles, general branch power (sales floor, restrooms, break room, exterior) | LOT | VERIFY | VERIFY | Device-level count not tallied in this pass — see E-1 Power Plan & E-2 Conduit/Power Plans for exact device locations; recommend detailed count pass if bid is close
31 | Restroom exhaust fan power wiring (fan furnished/installed by HVAC contractor, wired by APT) & motion-sensor-controlled lighting tie-in | EA | 2 | FIRM | E-1 Power Schedule item 'Exhaust Fan' + A1 Room Finish Schedule (2 restrooms)
6. SITE / UNDERGROUND / ALLOWANCES
ITEM | DESCRIPTION | UNIT | QTY | CONF. | SOURCE / BASIS / NOTES
32 | Underground primary/secondary electric service conduit & conductors, utility POC to service equipment — APT (ECFECI) | LOT | 1 | VERIFY | Route/length per Civil Composite Utility Plan C4.1 — not included in electrical sheet excerpt reviewed
33 | Transformer pad — coordinate with Duke Energy | EA | VERIFY | VERIFY | Utility-furnished per E-1 Service Entrance notes; APT coordinates conduit/pad prep — confirm scope split with Duke Energy requirements
34 | Site lighting underground conduit & conductors, pole bases to junction — APT (ECFECI) | LOT | 1 | VERIFY | Civil Photometric Plan PH0.1 — not included in electrical sheet excerpt reviewed
35 | Pylon Sign circuit — conduit, wire, and home-run connection only (cabinet/fixture by AutoZone sign vendor) | EA | 1 | FIRM | E-4 Panel A ckt18
36 | Side Wall Sign circuit — conduit, wire, and home-run connection only | EA | 1 | FIRM | E-4 Panel A ckt16
37 | Front Wall Sign circuit — conduit, wire, and home-run connection only | EA | 1 | FIRM | E-4 Panel A ckt6
38 | Allowances | — | NONE IDENTIFIED | VERIFY | No allowance line items found on electrical sheet set — cross-check AutoZone Required Bidding Breakdown (plan folder item 4.0/4.1) before pricing
7. LOW VOLTAGE INFRASTRUCTURE (CONDUIT & BOXES ONLY — wiring/equipment by others)
ITEM | DESCRIPTION | UNIT | QTY | CONF. | SOURCE / BASIS / NOTES
39 | Telephone system: empty conduit + J-box to 66 block backboard — APT (ECFECI); wiring by phone co./AutoZone contractor | LOT | 1 | FIRM | E-4 Alarm/Phone Board Requirements detail
40 | Data (Cat 5 / CrossCom) system: empty conduit + J-box, pull string — APT (ECFECI); cabling/termination by AutoZone's CrossCom contractor | LOT | 1 | FIRM | E-2 General Wiring & Power Note G
41 | Security/alarm system: empty conduit + J-boxes at door contacts, keypad, motion, pull stations, horn/strobe — APT (ECFECI); wiring by alarm contractor | LOT | 1 | FIRM | E-2 detail 6/7 — Overhead Door Alarm Reqs & Typical Man Door
42 | Thermostat (Venstar) system: empty conduit + pull string per RTU zone — APT (ECFECI); control wiring by mechanical contractor | EA | 2 | VERIFY | E-1 Work Included item D — one per RTU (2 RTUs); confirm exact box count on E-6
8. GROUNDING
ITEM | DESCRIPTION | UNIT | QTY | CONF. | SOURCE / BASIS / NOTES
43 | Ground rod system per NEC 250, resistance to ground ≤ 25 ohms | EA | 1 | FIRM | E-4 Detail 3 — Grounding/Bonding Diagram
44 | Grounding electrode conductor, #2 CU, min. 20'-0" from foundation bottom w/ 2" min. coverage | LOT | 1 | FIRM | E-4 Detail 3
45 | Building steel bonding jumper, #2 CU | EA | 1 | FIRM | E-4 Detail 3
46 | Interior metal water pipe bond, #2 CU (within first 5' if continuous 10'+) | EA | 1 | FIRM | E-4 Detail 3
47 | Equipment bonding jumper(s), sized per NEC | LOT | 1 | FIRM | E-4 Detail 3
48 | Communications bonding jumper, #6 CU | EA | 1 | FIRM | E-4 Detail 3
49 | Supply-side bonding jumper, #2 CU | EA | 1 | FIRM | E-4 Detail 3
LEGEND & KEY FINDINGS
Confidence key:
FIRM — read directly off a schedule, panel, or riser diagram (dimensionally/numerically stated on the drawings).
APPROX — visual symbol count from floor plans, stated as a ± range. Verify against CAD or a field walk before finalizing price on close bids.
VERIFY — partial or inferred; confirm against plans, other-trade schedules, or documents not included in this set.
SCOPE FLAG — OFEI, not ECFECI:
This project is Owner Furnished / EC Installed for panelboards, fused disconnects, breakers, ALL light fixtures, lamps, lighting control panel, occupancy sensors, photocells, control relays, ballasts, and site light poles/brackets. Confirmed on sheet E-1 ("Items Furnished by AutoZone") and Project Spec Division 16 ("16480 PANELBOARDS" / "16500 LIGHTING" both marked "AutoZone Furnished Contractor Installed"). Do not price fixture/gear procurement through Southern Lighting Source on this job — APT receives, inventories, and installs only.
Interior power poles are the one item this project assigns to APT to furnish (opposite of the OFEI pattern above) — confirmed by Summit GC's Scope Snapshot SOV under Electrical cost code 16000-000: "EC TO PROVIDE POWER POLES."
Fixture count methodology: Types A and B (the bulk of interior lighting) were counted visually from sheet E-3 by tracing chained fixture runs — flagged APPROX with a stated range. Type G (soffit downlights) was cross-checked against panel circuit load (E-4 ckt12, 392VA ÷ 49W = 8) and confirmed FIRM. If the bid comes down to the wire, re-verify A/B counts before committing to a firm fixture count with the field crew.
Not included in this plan set: Civil Photometric Plan (PH0.1) and Exterior Elevations (A2) were not part of the drawing excerpt reviewed — site light pole count/locations and exterior wall pack (Type D/L) split should be confirmed against those sheets before finalizing.