## Quantity Takeoff
EL CAR WASH 074 — LEHIGH ACRES, FL ¦ ELECTRICAL QUANTITY TAKEOFF
Accurate Power & Technology ¦ Job JS.07282026 ¦ Electrical drawings dated 05.19.26 (GC Permit Submittal); car wash equipment drawings dated 01.22.26
Building area: 3,569 SF gross footprint (SP101 Proposed Site Plan) ¦ 3,224 SF net interior (A701 Finish Schedule)
Interior breakdown: Car wash tunnel 2,061 SF ¦ Equipment room 797 SF ¦ MMC 149 SF ¦ Unisex restroom 71 SF ¦ Office 146 SF
ECFECI = Electrical Contractor Furnished, Electrical Contractor Installed.
ITEM | DESCRIPTION | UNIT | QTY | SOURCE / NOTES
1. SERVICE & DISTRIBUTION
1.1 | Service entrance assembly (ECFECI) — split main, 277/480V, 3PH, 4W. SE600: (2) 3" conduit, (2) 4#350 THWN Cu. SE400: (2) 2" conduit, (2) 4#3/0 THWN Cu | LOT | 1 | E-2.1 Riser Diagram
1.2 | Service disconnect (ECFECI), 600A, 3P, 277/480V, NEMA 3R — Main 1 of 2 | EA | 1 | E-2.1 Riser Diagram
1.3 | Service disconnect (ECFECI), 400A, 3P, 277/480V, NEMA 3R — Main 2 of 2 | EA | 1 | E-2.1 Riser Diagram
1.4 | Line gutter (ECFECI), 12" x 12", NEMA 3R | EA | 1 | E-2.1 Riser Diagram
1.5 | CT cabinet and meter socket (ECFECI), coordinated with FPL | EA | 1 | E-2.1 Riser Diagram
1.6 | Panel 'HDP' (ECFECI) — two sections, 480/277V, 3PH, 4W, surface mounted. Feeder SE1005: (3) 3" conduit, (3) 4#400 THWN Cu | EA | 1 | E-2.1 Riser Diagram / Panel List
1.7 | Panel 'CW' (ECFECI) — two sections, 225A, 120/208V, 3PH, 4W, surface mounted | EA | 1 | E-2.1 Riser Diagram / Panel List
1.8 | Transformer TR-75 (ECFECI) — 75 KVA, 480V Delta primary / 120-208V Wye secondary. Primary 3#1 Cu, 125A 3P; secondary 4#4/0 Cu, 225A 3P | EA | 1 | E-2.1 Transformer Schedule
1.9 | Motor Control Center — set, feed and wire the MCC serving the tunnel equipment | EA | 1 | WE-701 MCC Single Line Diagram
1.10 | Feeders from the MCC to tunnel equipment, complete with conduit, conductors and terminations | RUN | 8 | E-1.1 Electrical Floor Plan
1.11 | Three-phase equipment homeruns from panel 'HDP' — circuits 2/4/6, 7/9/11, 8/10/12, 13/15/17, 14/16/18, 19/21/23, 20/22/24 and 25/27/29 | RUN | 8 | E-1.1 Electrical Floor Plan
1.12 | Branch circuit breakers, feeder breakers and equipment disconnects (ECFECI) throughout | LOT | 1 | E-2.1 Panel Schedules
2. INTERIOR LIGHTING
2.1 | Type A — Beghelli BS100LED-4-HT-MO-WT40, 4' LED linear, surface mounted, wet location — tunnel line, standard | EA | 19 | A701 Luminaire Schedule / E-1.1
2.2 | Type A — same fixture, furnished with integral 90-minute emergency battery pack | EA | 19 | A701 Luminaire Schedule / E-1.1
2.3 | Linear LED fixture, equipment room — standard | EA | 1 | E-1.1 Lighting Floor Plan
2.4 | Linear LED fixture, equipment room — with integral 90-minute emergency battery pack | EA | 1 | E-1.1 Lighting Floor Plan
2.5 | Type B1 — HE Williams PT-22-L43-835, 2x2 LED recessed troffer, office — standard | EA | 1 | A701 Luminaire Schedule / E-1.1
2.6 | Type B1 — same fixture, furnished with integral 90-minute emergency battery pack | EA | 2 | A701 Luminaire Schedule / E-1.1
2.7 | Round surface mounted LED fixture, restroom | EA | 1 | E-1.1 Lighting Floor Plan
2.8 | Type X — Beghelli EPC-ATR LED exit sign with integral battery back-up, damp location | EA | 6 | A701 Luminaire Schedule / E-1.1
2.9 | Recessed LED downlights and wall sconces — tower entry, canopy soffit, office and restroom | EA | 16 | E-1.1 Lighting Floor Plan
2.10 | Wall mounted LED fixtures — building perimeter and equipment areas | EA | 8 | E-1.1 Lighting Floor Plan
2.11 | Dome and wall sconce LED fixtures — building perimeter and canopy soffit | EA | 15 | E-1.1 Lighting Floor Plan
2.12 | Canopy mounted LED fixtures — entry canopy and building overhangs | EA | 13 | E-1.1 Lighting Floor Plan
2.13 | Sign lighting connection — junction box and time clock, location coordinated with the sign supplier prior to rough-in | LOT | 1 | E-1.1 Lighting Floor Plan
2.14 | Tunnel signage and arch lighting — pipe lights (4), galaxy arch, arcade system, arcade panels (2) and grand arch, received and installed by the Electrical Contractor | EA | 9 | Car Wash Equipment Matrix
3. EXTERIOR / SITE LIGHTING
3.1 | Type A — LED wall pack, 15W, 4000K, forward throw, building mounted | EA | 10 | E-2.1 Luminaire Schedule / E-1.0
3.2 | Type B — LED wall pack, 10W, 4000K, forward throw, building mounted | EA | 4 | E-2.1 Luminaire Schedule / E-1.0
3.3 | Type C — LSI Lifestyle Medium XDLM decorative area light, 3000K, Type III distribution, pole mounted | EA | 3 | E-2.1 Luminaire Schedule
3.4 | Type D — LSI Lifestyle Medium XDLM decorative area light, 3000K, Type III distribution, pole mounted | EA | 2 | E-2.1 Luminaire Schedule
3.5 | Type E — LSI Lifestyle Medium XDLM decorative area light, 3000K, Type V distribution, pole mounted | EA | 1 | E-2.1 Luminaire Schedule
3.6 | Parking lot light pole assemblies — pole, augered base and backfill, hand-hole with in-line fuses and surge arrester per NEC 410.15, 1" PVC to pole and 5/8" x 8' copper-clad ground rod at each | EA | 6 | E-1.0 Site Plan / Pole Detail
3.7 | Vacuum canopy lighting — north canopy row | EA | 11 | E-1.0 Electrical Site Plan
3.8 | Vacuum canopy lighting — center canopy row | EA | 10 | E-1.0 Electrical Site Plan
3.9 | Precast concrete pull box, Brooks #36 with open bottom, at site lighting runs | EA | 6 | E-1.0 Pole Detail
4. LIGHTING CONTROLS
4.1 | Wall and ceiling mounted occupancy sensors — equipment room, control room, restroom and office | EA | 4 | E-1.1 Lighting Floor Plan
4.2 | Occupancy sensors — vacuum equipment enclosures | EA | 2 | E-1.0 Electrical Site Plan
4.3 | Photocell for exterior and site lighting control | EA | 1 | E-2.1 / E-3.1 Symbol Legend
4.4 | Lighting contactor and relay panel — exterior and site lighting circuits | EA | 1 | E-2.1 Riser Diagram
4.5 | Seven-day programmable time clock for sign lighting circuit | EA | 1 | E-1.1 Lighting Floor Plan
4.6 | Local switching — single pole, three-way and dimmer switches per plan | LOT | 1 | E-1.1 Lighting Floor Plan
4.7 | Functional testing of all lighting controls prior to final inspection | LOT | 1 | E-3.1 General Notes
5. BRANCH POWER — BUILDING
5.1 | GFI receptacles, 20A, 125V — equipment room, control room, restroom and exterior | EA | 9 | E-1.1 Electrical Floor Plan
5.2 | General purpose duplex receptacles — equipment and control rooms | EA | 5 | E-1.1 Electrical Floor Plan
5.3 | Duplex receptacles — office | EA | 5 | E-1.1 Electrical Floor Plan
5.4 | Weatherproof receptacles — site and vacuum islands | EA | 6 | E-1.0 Electrical Site Plan
5.5 | Wall exhaust fan connections at 80" A.F.F., including switching | EA | 5 | E-1.1 Electrical Floor Plan
5.6 | High volume ceiling fan connection, including control | EA | 1 | E-1.1 Electrical Floor Plan
5.7 | FCU-1 fan coil unit — power, disconnect and connection | EA | 1 | E-1.1 / Mechanical Schedules
5.8 | DFCU-2 ducted fan coil unit — power, disconnect and connection | EA | 1 | E-1.1 / Mechanical Schedules
5.9 | EWH-1 and EWH-2 electric water heaters — power, disconnect and connection | EA | 2 | E-1.1 Electrical Floor Plan
5.10 | Hand dryer, electric water cooler and telephone backboard connections | EA | 3 | E-1.1 Electrical Floor Plan
6. BRANCH POWER — CAR WASH EQUIPMENT
6.1 | Blower motor — 15HP, 480V, 3PH, 40A breaker | EA | 11 | Car Wash Equipment Matrix
6.2 | High pressure pump — 15HP, 480V, 3PH, 40A breaker | EA | 2 | Car Wash Equipment Matrix
6.3 | Air compressor — 10HP, 480V, 3PH, 25A breaker | EA | 3 | Car Wash Equipment Matrix
6.4 | Reclaim unit, combination power pack and twin conveyor power pack — 10HP, 480V, 3PH, 25A breaker | EA | 3 | Car Wash Equipment Matrix
6.5 | Prep gun pump — 7.5HP, 480V, 3PH, 20A breaker | EA | 1 | Car Wash Equipment Matrix
6.6 | Reclaim and repressurization pumps — 5HP, 480V, 3PH, 15A breaker | EA | 4 | Car Wash Equipment Matrix
6.7 | R.O. repressurizer and R.O. reject pump — 3HP, 480V, 3PH, 15A breaker | EA | 2 | Car Wash Equipment Matrix
6.8 | Mitter motor — 2HP, 480V, 3PH, 15A breaker | EA | 1 | Car Wash Equipment Matrix
6.9 | Wrap, omni and top brush motors — 1HP, 480V, 3PH, 15A breaker | EA | 7 | Car Wash Equipment Matrix
6.10 | R.O. filtration system — 2HP, 220V, 1PH, 15A breaker | EA | 2 | Car Wash Equipment Matrix
6.11 | Air dryer, 75 CFM — 3/4HP, 120V, 1PH, 25A breaker | EA | 2 | Car Wash Equipment Matrix
6.12 | Commercial washer — 208V, 1PH, 20A breaker, with service disconnect | EA | 1 | Car Wash Equipment Matrix
6.13 | Vacuum producer panels — 480V, 3PH, 80A breaker each | EA | 2 | Car Wash Equipment Matrix
6.14 | Miscellaneous 120V equipment circuits — carbon tanks, reject water storage tank and conveyor controller, 20A breaker | EA | 3 | Car Wash Equipment Matrix
6.15 | 120V point-of-sale and signage circuits, 20A breaker — pay stations, POS gates, pipe lights, arches, arcade panels and instructional signage | EA | 17 | Car Wash Equipment Matrix
6.16 | 24V solenoid, sensor and control device terminations from the MCC and tunnel controller — photo eyes, tire switches, emergency stops, anti-collision devices, solenoid valves and control panels | EA | 74 | Car Wash Equipment Matrix
6.17 | Local equipment disconnects (ECFECI) as required by NEC beyond those furnished with the car wash equipment | LOT | 1 | WE-411 Motor Power Plan
7. SITE / UNDERGROUND / ALLOWANCES
7.1 | Underground site lighting branch circuits — rigid non-metallic conduit, Schedule 80, minimum 24" below grade, with trench and selected backfill | LOT | 1 | E-1.0 Pole Detail / E-3.1 General Notes
7.2 | Underground feeders to vacuum canopy lighting and vacuum producer panels | LOT | 1 | E-1.0 Electrical Site Plan
7.3 | Underground service lateral from the utility transformer to the service disconnects, with 8' of conductor slack at the transformer secondary | LOT | 1 | E-2.1 Riser Diagram
7.4 | Allowance — site pole base excavation, augered holes and crushed rock, coordinated with the site contractor | ALLOW | 1 | E-1.0 Parking Lot Pole Detail
7.5 | Allowance — coordination of easements, existing underground utilities and drainage prior to drilling pole bases | ALLOW | 1 | E-1.0 Parking Lot Pole Detail
8. LOW VOLTAGE INFRASTRUCTURE (CONDUIT & BOXES ONLY)
8.1 | Security camera conduit, boxes and pull strings — cameras, cabling and programming by Owner's vendor | LOT | 1 | Low Voltage Camera Conduit Drawings
8.2 | Car wash network and point-of-sale data conduit and boxes — devices, cabling and programming by vendor | LOT | 1 | WE-703 Network Diagram
8.3 | Telephone backboard conduit and feed | EA | 1 | E-1.1 Electrical Floor Plan
8.4 | Equipment room cable tray — coordination and support by the Electrical Contractor | LOT | 1 | WQ-412 Cable Tray Layout
9. GROUNDING
9.1 | Grounding electrode conductor, #2 Cu, with bonding to metal water piping, building steel and ground ring | LOT | 1 | E-2.1 Riser / E-3.1 Ground Detail
9.2 | Ground rods, 5/8" x 10' copper-clad, spaced 6'-0" apart, at the service | EA | 2 | E-3.1 Ground Rod Detail
9.3 | Concrete-encased electrode — #4 or larger bare copper, minimum 20' in footing | LOT | 1 | E-3.1 Ground Detail
9.4 | Ground bus bar, 1/4" x 4" x 12", in electrical, MMC and telephone rooms | EA | 3 | E-3.1 Ground Bar Detail
9.5 | Ground rods, 5/8" x 8' copper-clad, one at each site light pole | EA | 6 | E-1.0 Parking Lot Pole Detail
9.6 | Equipment grounding conductors — green insulated, all feeders and branch circuits | LOT | 1 | E-3.1 General Notes