PRE-BID PACKAGE — INTERNAL USE

Accurate Power & Technology — Central FL Region

Date: July 23, 2026

To: Sam (Estimator)

From: Alex Example, Commercial A.E.

Re: Indian Oaks Self Storage — Wildwood, FL — Pre-Bid Package

GC / Client: Bay to Bay Properties

Address: 789 Example Way, Springfield, IL 62701

Owner/Developer: Shadowbrook Development (Self-Storage and Industrial Real Estate), Longwood, FL

Engineer of Record: Land Investment Services, LLC (LIS) — Pat Roe, PE #00000

Plan Date: 06/26/2026  |  Received: 07/13/2026 (Initial Bid Set 26.0713)  |  Engineer Project No. 2025-015

Job No.: JS.07232026

NOTE: The architectural/engineering drawing title blocks and E-series sheets identify this project as “SHADOWBROOK STORAGE FACILITY.” Bay to Bay Properties' own drawing log names it “Indian Oaks Self Storage – Wildwood, FL” at the same address (789 Example Way, Springfield, IL 62701) — same site, likely a project rename. Confirm which name to use before the bid goes out.

This package covers the full electrical scope for review and takeoff. Quantities marked “TBD — verify” in the attached takeoff sheet require a visual count from the full drawing set (Area A + Area B, both floors) — text extraction only reliably pulled the photometric/site lighting schedule, the riser diagram, and the panel/service sizing. E100 (Electrical Specifications, 9.9 MB) would not text-extract at all; open it directly from OneDrive for the written spec sections.

SCOPE OF WORK

- The project is understood to be electrical work and has been reviewed and quoted as such.

- All work to be completed during normal business hours, 8:00 AM – 4:00 PM, Monday through Friday.

- Installation per plan. All changes will require a written Change Order approved by the Owner before work proceeds.

- Based on the electrical specifications, schedules, and drawing set dated 06/26/2026. Sheets: E100, E101, E102, E103, E104, E105, E106, E200, E201, ES100, ES101.

- Coordinate with Bay to Bay Properties (GC) and other trades for scheduling, tie-ins, and required access.

- Submit for and obtain all required electrical permits prior to commencement of work.

A. Service & Distribution

- 1,000A, 277/480V, 3-phase, 4-wire service entrance assembly and MDP (ECFECI), fed by (4) sets of 4–#500 AL in 3-1/2" conduit from the utility transformer to a single-point-ground meter/main disconnect location.

- Distribution gear (ECFECI): Panels L1 & L2 (400A MLO, 120/208V, 3PH/4W) fed from the service; Panels H1a/H1b and H2a/H2b (HVAC distribution, 400A MLO / 200A MCB, 120/208V) fed via a 75 kVA step-down transformer (277/480V to 120/208V), with feeders and disconnects throughout.

- Two (2) elevator disconnects, 200A, 277/480V, NEMA 3R, per riser diagram (Sheet E200).

- Complete grounding and bonding system per NEC, including Ufer ground / concrete-encased electrode, ground rods, and 3/0 AWG copper grounding electrode conductors at the service and step-down transformer.

B. Branch Power

- Branch circuit wiring and devices for storage-unit lighting/occupancy-sensor switching, corridors, stairwells, and common areas per plan.

- Branch power and dedicated circuits for office/leasing area equipment: HVAC disconnects and thermostats, elevator cab/controller/telephone/fire-alarm circuits, water heaters (IWH-1, IWH-2), microwave, refrigerator, exhaust fan interlock, recessed TV outlet, podium/millwork receptacles, monument sign connection, and POS system with dedicated isolated-ground circuit.

C. Lighting & Controls

- Complete lighting package (ECFECI) — procured through the Southern Lighting Source national account (555-555-0100). EC to receive, inventory, and install all fixtures per schedule, interior and exterior/site.

- Controls & testing: time clock and photocell control of all interior/site lighting per Florida Energy Code, occupancy-sensor switching at each storage unit and office space, daylight-harvesting sensor at the show window, motion-sensor exterior fixtures; functional testing prior to final inspection.

- Fixture types per schedule: L1, L2, L2E, L6, L7E, L9, L9E, L15, V, X1, EG, XE (interior — Sheet E106); WS, WP, PA3, PA5 (site/exterior — Sheet ES100).

D. Site Lighting, Underground Work & Allowances

- Site lighting per photometric plan (Sheet ES100): 52 wall sconce (WS), 9 wall pack (WP), 3 pole-mount area light – 3 lamp (PA3), 2 pole-mount area light – 5 lamp (PA5); fed from Panel L1 site-lighting circuits.

- Underground site power/lighting conduit and conductor per riser and site power plan (Sheet ES101); feeder runs shown up to 640 LF — confirm total footage against the full site plan.

- Allowance: Monument/pylon sign electrical connection (coordinate exact requirements with Civil).

- Allowance: [Jake to confirm any additional site allowances — none identified beyond the monument sign in the current set.]

E. Low Voltage Infrastructure (Conduit & Boxes Only)

- Conduit and boxes only for low-voltage systems: security cabinet/camera rough-in, 2-way call box back to telephone backboard, recessed TV/data outlets, elevator 2-way communication, fire alarm device conduit — devices, cabling, and programming by Owner's vendor.

F. Project Coordination & Closeout

- Coordinate with GC and other trades — mechanical (AC/CU connections, thermostats), fire protection (flow/tamper switches), elevator installer, and security/POS vendors — for rough-in and final connections.

- Provide final testing, labeling, and closeout documentation to support permit close-out and Owner turnover.

See attached Indian_Oaks_Self_Storage_Quantity_Takeoff.xlsx for the full 8-category takeoff. Populate the “TBD — verify” rows from the full drawing set before pricing.