PRE-BID PACKAGE — INTERNAL USE ONLY

Date: 07/23/2026

To: Sam (Estimator)

From: Alex Example, Commercial A.E., Central FL Region

GC: Bay to Bay Properties

Re: Nick & Moe's Convenience & Liquor Store

Address: 321 Example Ave, Springfield, IL 62701  (site plan sheets E1.0/E1.1 reference “654 Example Hwy, Springfield, IL 62701” — same corner lot; confirm official address with GC)

Owner / Engineer: Owner not identified in drawing set. Engineer of record: MDM Services, Inc. — Pat Roe, P.E. (FL #00000); fuel island electrical by Alex Example, P.E. (FL #00001). MDM Job #25039.

Plan Date(s): 08/06/2025 (base electrical set, E0.0–E6.1); 06/03/2026 (fuel island electrical addendum, GE1.0 & SE1.0). Received from GC 07/16/2026 as Initial Bid Set.

Sheets: E0.0, E0.1, E1.0, E1.1, E2.0, E2.1, E2.2, E2.3, E3.0, E3.1, E3.2, E3.3, E4.0, E4.1, E5.0, E5.1, E6.0, E6.1, GE1.0, SE1.0

Job Number: JS.07232026

Internal scope review — price against the accompanying Nick_Moes_Quantity_Takeoff.xlsx. This is not a proposal; do not release externally.

Rev.1 (07/23/2026): scope firmed up after review of E5.1 panel schedules, E3.0 lighting plan, E2.0/E2.1 power plans, E1.0 site plan, and SE1.0 fuel island. Panel count, distribution, and fuel dispenser count are now confirmed.

SCOPE OF WORK

- The project is understood to be electrical work for a new 6,310 SF convenience store with liquor sales, Pizza Hut and Quiznos food service counters, and an attached fuel canopy/dispenser island; reviewed and quoted as such.

- All work to be completed during normal business hours, 8:00 AM – 4:00 PM, Monday through Friday.

- Installation per plan. All changes will require a written Change Order approved by the Owner before work proceeds.

- Based on the electrical specifications, schedules, and drawing set dated 08/06/2025 (base electrical) and 06/03/2026 (fuel island electrical addendum). Sheets: E0.0, E0.1, E1.0, E1.1, E2.0, E2.1, E2.2, E2.3, E3.0, E3.1, E3.2, E3.3, E4.0, E4.1, E5.0, E5.1, E6.0, E6.1, GE1.0, SE1.0.

- Coordinate with Bay to Bay Properties (GC) and mechanical, plumbing, low-voltage/security, and fuel equipment (Carolina Products / CPI) contractors for scheduling, tie-ins, and required access.

- Submit for and obtain all required electrical permits prior to commencement of work.

A. Service & Distribution

- New 1,200A, 120/208V, 3-phase, 4-wire electrical service, including service entrance assembly, utility metering CT cabinet, and MDP (ECFECI), fed by the serving utility (Duke Energy — verify point of connection in field).

- Distribution gear (ECFECI): nine panels total. Unitized MDP/MTS/CT switchgear package by Carolina Products, Inc. (CPI) houses Panels P1, P2, P3, L, G, and E2 (all 225A MLO, 208Y/120V, 3PH, 4W, 65kAIC). Three additional surface-mounted NEMA-1 panels: Panel R (store receptacles/lights, RTU-3, tankless water heaters), Panel E1 (walk-in cooler/freezer condensers), and Panel ST (fed with a 200A shunt-trip breaker, serving all hood-interlocked kitchen fryers). Feeders and disconnects throughout; manual transfer switch (MTS) for a future portable generator connection (generator by others).

- Grounding electrode system, TBB intersystem ground bus bar, and panel ground bus bars per NEC 250 and E4.x grounding details.

B. Branch Power

- Branch circuit wiring and disconnects for all C-store, Pizza Hut, and Quiznos kitchen, beverage, and refrigeration equipment per the E2.2/E2.3 equipment schedules (~55 items, including reach-in and walk-in coolers/freezers, beer cave, ovens, fryers, coffee/beverage equipment, ATM, lottery machine, hand dryers, digital menu boards, and water heaters).

- Roof-mounted RTU-1/2/3, kitchen exhaust/supply fans (KEF-1, KSF-1), and six remote condensing units with disconnects, motor-rated switches, and weatherproof GFI maintenance receptacles per E3.3.

C. Lighting & Controls

- Complete lighting package (ECFECI) — procured through the Southern Lighting Source national account (555-555-0100). EC to receive, inventory, and install all interior, site, and fuel canopy fixtures per schedule (E3.1 interior; E1.1 site/photometric).

- Controls & testing: nLight DLM occupancy/daylight sensors, power packs, and time-of-day gateway for interior lighting; photocell/contactor control for exterior building and site lighting; 5-unit emergency lighting battery inverter system (2 racks) with EPC relays; functional testing prior to final inspection.

- Fixture types per schedule — Interior (E3.1): A, C, D, E, F, G, K, LP1, N, M, X, LE (counts taken from E3.0 plan; E3.1 has no quantity column). Site/Canopy (E1.1 photometric, firm quantities): A, B, C, D, E, W.

D. Site Lighting, Underground Work & Allowances

- Site/canopy pole and canopy lighting allowance — 49 fixtures per photometric schedule (12 Type A + 24 Type B canopy fixtures; 4 Type C + 1 Type D + 3 Type E pole area lights; 5 Type W wall packs).

- Fuel island electrical: 10 dispenser positions (5 islands × 2) — power/data/monitoring conductors per dispenser; canopy lighting circuit; Veeder-Root TLS-450 tank monitoring console; three USTs (20K Regular, 12K Diesel, 8K Premium) with STP connections; (3) remote emergency fuel shut-off stations plus cashier E-stop; and intercom wiring per GE1.0/SE1.0.

- Site underground conduit/wire allowance for pole and canopy feeders per the E1.0 conduit/wire schedule — the schedule is vector-drawn and would not extract; footages to be scaled off E1.0 directly (still open).

- Building sign circuit allowance, routed through exterior lighting contactor per E4.1 detail.

- All underground conduit minimum 24" burial depth with warning tape; wiring in EMT/PVC conduit, all homeruns hard-piped.

E. Low Voltage Infrastructure (Conduit & Boxes Only)

- Provide conduit and boxes only for POS/data, security camera, intercom, and fuel dispenser communication systems — TBB backboard, IT rack conduits, and floor boxes at the cashier counter and order station per E2.0/E2.1. Cabling, devices, and programming by Owner's low-voltage vendor.

F. Project Coordination & Closeout

- Coordinate with mechanical (RTU/condenser connections), plumbing (water heater/recirculation pump), equipment installers (coolers, ovens, POS, millwork), and the fuel equipment contractor (Carolina Products/CPI) for tie-ins and connection points.

- Provide O&M manuals, panel directories, as-built markups, and lighting control functional testing/training per E0.1 specifications prior to final acceptance.

EXCLUSIONS & CLARIFICATIONS

- Fuel tank and piping installation (TK-series sheets) excluded — by fuel systems/UST contractor. EC scope is limited to the fuel island electrical (GE1.0/SE1.0) only.

- Utility company primary-side work, transformer, and utility fees excluded.

- Portable generator excluded (by others) — EC provides MTS connection point only.

- Low-voltage cabling, devices, and programming (security, POS network, intercom, sound) excluded — by Owner's vendor; EC provides conduit and boxes only.

- Painting, patching, concrete cutting, and finish restoration excluded.

- DISCREPANCY — Building area/address: electrical title blocks list 6,310 SF at 321 Example Ave, Springfield, IL 62701; site plan sheets E1.0/E1.1 list 6,332 SF at 654 Example Hwy, Springfield, IL 62701. Appears to be the same Delmar Drive/US Hwy 19 corner lot — confirm official address and area with GC/architect before final GMP.

- RESOLVED — Panel R: confirmed on E5.1 as a 225A MLO, 208Y/120V 3PH surface-mounted (NEMA-1) panel serving store receptacles/lights, RTU-3, and (2) tankless water heaters. It was absent from the E6.1 unitized-cabinet list only because it is surface mounted (as are Panels E1 and ST) — not a discrepancy.

- STILL OPEN (VERIFY in takeoff): (1) E1.0 site underground conduit/wire footages — vector-drawn schedule, scale off the sheet; (2) security-camera J-box count — coordinate with security vendor; (3) Type M tower LED-strip length — per architectural A-102; (4) interior fixture quantities are plan-symbol counts (E3.1 carries no quantity column) and are APPROX with ± ranges — spot-check the Type N sales pendant (~30) before final GMP.